GT100-C

WORK BY OTHERS

PROJECT #: _______

PROJECT NAME: __________________

PROJECT MANAGER: ___________

REFER TO THIS DOCUMENT BEFORE

ANY INSTALLATION AND BEFORE

APPROVING THE FOLLOWING DRAWINGS

1. GENERAL

  - Scope

Provide all labour, materials and equipment required to install a handicap hydraulic and cable (2:1) elevator, model GT-100C HD commercial type, manufactured by Global Tardif Elevator Manufacturing Group inc. (hereafter called the Manufacturer) as shown on the drawings and specifications.

The Manufacturer will supply shop drawings, materials and equipment to the installer company. Elevator construction works shall not start before drawings have been approved by the owner or general contractor.

The Manufacturer is located at 120 de Naples, St-Augustin de Desmaures, Québec, Canada (T. 418 878 4116 or le 1.800.661.6316; Fax 418.878.1595).

  - Preparatory work done by others

To complete the elevator installation, some other works have to be done by others:

- All masonry work, gyproc and paint.

- A steel girder installed on the hoistway ceiling to lift elevator equipment during installation.

- Hoistway has to be built as per elevator shop drawings, (structural reinforcing, ventilation etc…) and must follow all applicable codes and standards.

- The pit depth minimum standard is 10’’ (254 mm). The pit shall be clean and built as per code regulations. Provide pit waterproofing or sump pumps if required. Provide adequate support for guide rail fastenings.

- Provide a level concrete pit floor to support the required load impact.  To know the support load impact, do the following calculation:

Gross load (capacity + cab weight) x 2, 5 = Support load impact (as per chapter 1 of construction code).

Support Load Impact = _____ lbs (Please Complete)

N.B.: See at:  http://www.gtaccessibility.com/CabWeightChart.pdf the Cabin weight Chart for each model.

- Hoistway walls, to be built square and plumb all over height with a maximum tolerance within ¼’’ (6mm). Hoistway walls, with smooth interior surfaces without any bumps.

- Provide a lockable room to store elevator parts and equipment before and during installation.

- Machine room to meet or exceed Canadian C.E.C. and CAN-CSA-B355-09 codes and other standards. Provide a light and light switch 110 VAC with a minimum of 100 LUX luminosity at floor level as per regulations. A lockable, exterior opening fire rated door equipped with an automatic door closer, will secure the access of the machine room.

- Appropriate overhead from upper landing floor up to the hoistway ceiling or under the steel girder as per elevation drawing from Global/Tardif.

- During installation, hoistway landings access to be fully open at least 8 feet high.

- Cab floor finishing and installation by others (Maximum load: 2 lbs/square foot).

- Rough openings for landing floor call stations and signage, as per drawings.

- Electric power for setting and test on first installation day by electrical contractor.

- As per National U.S. electric code or Canadian electric code, a fuse disconnect switch for each elevator connected to a 30 amp circuit equipped with a normally open type contact.

- As per the same codes, 15 amps, 110 volts, 60 hertz disconnect switch for the cab light is installed as indicated on shop drawings. Install 2 wires and one ground from the disconnect box to the controller connections.

- Following section 38 of the electric Canadian codes, install an auxiliary contact in the principal disconnect switch.

- The disconnect switch is install 20 feet away maximum from the controller and is visible from there. If not, a second disconnect switch shall be installed near the controller.

- Electric power have to be plug to a fuse main disconnect box with a manual exterior lever OR to a non-fused disconnect box lockable at ON or OFF position. That disconnect box should be located as per our layout drawing.

If a 208/230/1phase/60HZ motor is used, and if the building electric power available is

240/1phase/60HZ, 2 wires + 1 neutral +1 ground have to be connect from the disconnect

box to the controller. Provides building disconnect box 30 amps with an auxiliary contact

NC/NO  fused 25 amps type D.

If a 208/230/1phase/60HZ motor is used, and if the building electric power available is

208v/3phases/60HZ, 2 wires + 1 neutral +1 ground have to be connect from the

disconnect box to the controller. Provides building disconnect box 30 amps with an

auxiliary contact NC/NO  fused 25 amps type D.

If a 208/230/1phase/60HZ motor is used, and if the building electric power available is

600v/3phases/60HZ and if a transfo is supply with the job, 2 wires + 1 ground from

building disconnect box to transfo and, 2 wires + 1 neutral + 1 ground from transfo to

controller should be connected. Provide building disconnect box 15 amps with an

auxiliary contact NC/NO  fused 15 amps type D.

N.B. It is owner &/or general contractor responsibility to validate final amperage as per elevator electric drawings

- If a 600v/3phases/60HZ motor is used, and if the building electric power available is 600v/3phases/60HZ, you will have to provide 3 wires + 1 ground from building disconnect box to controller. Provide building disconnect box 15 amps with auxiliary contact NC/NO fused 6 to 7 amps type D.

Only elevator equipment and elevator electric pipes are allowed in the machine room.

N.B. It is owner &/or general contractor responsibility to validate final amperage as per elevator electric drawings

- A temperature between 15 and 32 Celsius has to be constantly kept in the machine room.

- Light, light switch and electric outlet in the hoistway and machine room are required before starting elevator installation.

## IMPORTANT

- The elevator drawings are made in accordance with the CAN-CSA-B355-09 codes.

- These drawings are not done for the building construction. They are to illustrate the relation between the elevator and the structure.

- This drawing is only for the installation. The landing door details and cab details will be on separate pages.

- Global/Tardif is not responsible for the exact details and dimensions of the hoistway structure and the machine room.

- The owner/buyer/builder will provide suitable lintels over and under landing entrances.

- The doorframes are not built to support the weight of the walls. The general contractor is responsible for any damages caused by masonry and finishing works around the landing doors.

- The total distance between the lower and the upper floor, as per the elevation drawing, has to be maintained within ¼’’ (6mm).

- Provide adequate support for guide rail fastenings or for tower supports as per shop drawings.

- Provide finish grouting and masonry around doorframes only after the end of their installation.

  - Warranty

The Manufacturer’s acceptance is conditional on the understanding that their warranty covers defective material. The guarantee period shall not extend beyond one year from the date of completion or acceptance thereof by beneficial user, whichever is earlier, of each elevator. The guarantee excludes ordinary wear and tear of improper use, vandalism, abuse, misuse, or neglect or any other causes beyond the control of the Manufacturer and this express warranty is in lieu of all other warranties, express or implied, including any warranty of merchantability or fitness for a particular purpose.

Labour is guaranteed for one year by the installer.

  - Maintenance

The Elevator Installation Company will provide a quality maintenance contract including verifications, adjustment and lubrication of the equipment regularly every 3 months after the elevator delivery day (we recommend a monthly maintenance for units subject to extensive operation). The maintenance shall be done by skilled mechanics during day worktime. Urgent calls will be carried out during normal daytime. Maintenance contract will not cover service calls caused by negligence, abusive use or accidents caused by others than the elevator installer. Only original elevator parts can be used for repairs.

  - ‘Corrostop-2000’ Paint finish

The elevator manufacturer will paint all exposed parts without finish with GT-CorroStop-2000 process.

  - Permit/ Inspections

The elevator installer will attend to all inspections and verifications required by authorities. The owner will be responsible for the cost of any license issued by government inspectors.

  - Codes

All works have to be done in accordance with the Canadian Electrical Code, Provincial Elevator code and CAN/C.S.A.-B355-09 standard as well as any local code applicable. The manufacturer is not responsible for any changes in regulations or codes.

2. PRODUCTS

2.1 Description

| Furnish and install: | One (1) hydraulic and cables (2:1) elevator model : GT100-C HD manufactured by Global Tardif inc. |
| --- | --- |
| Operation: | # Constant pressure |
| Control type: | Simple relay controller model GT-EZ100 |
| Capacity: | Maximum: 1000 lbs (454 kg)) |
| Normal speed: | 30 fpm (0,15m/s) |
| Travel: | ____ Ft ____ in. (Please Complete) Maximum 23 feet (7 meters) |
| Pit : | ____ in. (Please Complete) Standard Minimum: 10 ‘’ (254 mm) |
| Overhead : | ____ in. (Please Complete) Standard Minimum: 96’’ (2438mm) |
| Hoistway net dimensions: | Width : ____ ft ____ in. (Please Complete) Depth : ____ ft ____ in. (Please Complete) (Look for standard dimensions at www.gtaccessibility.com) |
| Platform dimensions : | Look for standard dimensions at www.gtaccessibility.com |
| Net cab dimensions : | Width : ____ ft ____ in. (Please Complete) Depth : ____ ft ____ in. (Please Complete) (Look for standard dimensions at www.gtaccessibility.com) (maximum 21,5 sq.feet) |
| Nbr. of Stops | ____ Stops Please Complete) |
| Opening type for each Stop | (Please enter the stop number for each opening types ex.: Front Only: Stops #1-2-3, Front/Rear: Stop #4) Opening; Stops (ex.: #1-2-3). Front Only. Front & Rear. Front & Side. Side Only. |
| Landing door net standard size: | 36’’ (914mm) width’’ 80’’ (2032’’) height |
| Door entrance dimension | 36’’width (914mm) x height 80’’(2032mm) |
| Type of doors | Hinged swing door model GT-Swing Door |
| Doors operation: | Manual opening (motorized opening in option) |
| Cab height : | 80’’ (2032mm) |
| Car operating panel: | Stainless steel plate (1/8’’) Thickness |
| Landing call stations : | ABB Chrome framing raised push buttons |
| Power supply: | (208, 220, 230, 240, 440, 460, 480, 550, 575 & 600) Volts, 3 Phase, 60 Hz OR 220 Volts, 1 Phase, 60 Hz ____ Volts / ___ Ph / ___ Hz. (Please Complete) |

2.2 Mechanical Structure and hydraulic system

The one side cantilever mechanical structure shall include a steel corrosive proof mechanical system manufactured with high-tech machinery using numeric and laser technology. Inside the structure is the hydraulic system, the guide rails, rail supports, guide shoes and the car sling.

- The guide shoes shall easily slide along the 8 lbs/feet ‘’T’’ steel guide rails. These rails shall be installed plumb all over the elevator hoistway height.

- Adjustable ‘’C’’ rail brackets will ensure rail plumb and stability in case of any bumps on the supporting wall.

- Provide guide shoes with TIVAR inserts type UHMW.

- The car sling shall be fabricated from painted steel members with adequate bracing to support the platform, the traction cables and the cab.

The hydraulic system shall include a cylinder, plunger, hydraulic hoses, motor, pump, valve and traction cables.

- The cylinder shall be manufactured from a steel pipe with a sufficient thickness and suitable safety margin. The top of the cylinder shall be equipped with a cylinder head with an internal guide-ring and self-adjusting packing.

- Provide a plunger, manufactured from a steel shaft with a proper diameter machined true and smooth. The plunger shall be provided with a stop electrically welded to the bottom to prevent it from leaving the cylinder.

- Provide a 1/2’’ (12,7 mm) hydraulic rubber hose with all equipments and fittings for good elevator operation.

- Provide a 3 HP minimum submersible type motor and install it inside the oil tank in the machine room.

- Provide a GT-100SB Power submersible type pump allowing enough oil flow to move the cab in an UP direction easily and install it in the oil reservoir in the machine room. Use flexible fittings only.

- Be sure to provide a valve good enough to ensure exact oil pressure to move the elevator up. Install it in the oil reservoir.

- Provide a minimum of two (2) type 3/8’’ (9, 5 mm) diameter 8x19 steel cables. They shall be fixed at the cylinder base and at the car sling passing by a 10 ¾’’ 
(273 mm) diameter pulley attached at the top of the cylinder.

2.3 Pump unit

- Pump unit shall include: the oil reservoir, the submersible motor and pump and the valve.

- Provide a steel paint reservoir mounted on four (4) solid steel legs strong enough to support the weight of the oil, the motor, the pump and the valve.

- The valve shall be equipped with an adjustable pressure relief system, a manually operating down system to lower the elevator if emergency and a system to isolate the cylinder from the pump unit plus a check valve for down control operation.

- Provide a negative pressure switch that will be activated when negative pressure is sensed in the hydraulic system. The check valve will close and stop the hydraulic jack from descending immediately on sensing negative pressure.

2.4 Flow control

Provide a flow control system in case of hydraulic hose rupture.

2.5 Thrust block (end of travel)

Provide thrust blocks at the lower end of the rail to automatically stop the cab. A cylinder thrust block will stop the cab when going up.

2.6 Controller

Controller shall consist of a micro-processor type GT-EZ100 from Global/Tardif.

The controller shall include a UPS system to lower the elevator in case of power failure.

2.7 Levelling Device

- The elevator shall be provided with a 2 way-levelling device, which will maintain the car within ½’’ (13 mm) of the landing, by mechanical switches.

- Levelling device switches shall be located in a position to be inaccessible to unauthorized persons.

2.8 Platform

The platform shall be built on a steel frame with one plywood sheeting (1 x ¾’’ (19 mm)

It shall be installed on the car sling where the floor finish and the cab walls will be mounted.

The Manufacturer will provide a platform satin coated toe guard.

  - Cab

1.    Walls: MCP melamine panels 5/8’’ (16mm) two (2) standard colours.

(Plastic laminated available in option)

2.   The wall installed on the car sling side shall be detachable to allow easy access for

maintenance.

- Handrail: a single #4 stainless steel with both ends attached to the wall shall be

located on the wall panel in front of the control station.

- Floor finish: rubber flooring (diamond plate mat black) supplied by the manufacturer or supplied by others according to the architect’s choice.

- Ceiling:  Solid white melamine panel (5/8’’ (16mm)) with two (2) recessed pot lights and access for maintenance

- Install an emergency buzzer in the cab control station.

7.   A fixed cam for the landing door locks will be installed on the cab structure.

(Retractable cam in option)

N.B. A large variety of finish and accessories are available in option.

2.10 Telephone cabinet or hand-free phone

Install a stainless steel outside finish telephone cabinet in the cab.

Note: Telephone to be provided by others.

Or option

Provide a hand-free phone mounted in the car operating panel.

The travelling cable between the cab and the controller shall include necessary wires for telephone connection. Allow a minimum of 10 % extra wires.

The owner should provide connection from a telephonic central or assistance headquarters to the machine room near the controller.

2.11 Car operating panel

Car operating panel shall be #4 stainless steel finish flush mounted with a constant pressure push button, emergency alarm, emergency light and a key operation switch. The key shall be removable when it’s in OFF position only.

2.12 Hall stations

Each hall station shall include constant pressure illuminated push buttons

2.13 Swing landing doors (including frame and interlock)

- Provide primed steel door frames at each landing.

- Provide an anti-skid sill for each landing entrance.

- Provide a GT Swing Door for each landing entrance, manufactured with a 3’’ (77 mm) width x 23’’ (589 mm) high wire mesh sight glass, held by two (2) hidden hinges, built to fit 5 ¾’’ masonry walls.

- The elevator installer will take on full responsibility for the doors and door frames installation.

- The door assembly shall be code appliances UL/ULC labelled.

.

- The door shall be equipped with a GAL Type N and a delay door closer (Automatic door opener in option).

3. INSTALLATION

3.1 Coordination

Execute all works in accordance with other sub-contractors.

3.2 Finish

- Remove all rust on the elevator structure and coat with CorroStop-2000 paint finish process.

- Also coat with steel enamel paint all other equipments such as cylinder, rail supports, etc…

- It is forbidden to use point welding assembly procedure because it could cause visible imperfections or damages on stainless steel finishes.

- Cover finished materials with plastic protection covering.

3.3 Touch up

- If any damages appear on materials at the end of the installation, please make any touch ups if necessary.

- Remove all plastic protection covering and clean all surfaces to leave the job impeccable.

3.4 Field test

- Make all the tests prescribed by the CAN/C.S.A. B355-09.

- Provide all equipments and instrumentations to do such tests.

- Provide all certifications and test certifications for legal authorities.

- Please advise one (1) week in advance for the date and time of field tests.

- Keep one copy of job specifications on field for the chief elevator installer.

3.5 Welding

Any field bridge welding should be identified with the name of the welder.

3.6 Blowtorch use

It is important to not use cutting blowtorch for any reasons. If any burnt pieces of work  is detected, the job will be rejected.

THE END